## PRG7A
br./Item | Opis opreme i radova |  |  | Description of equipment and works | veličina/ Unit | količina/ Quantity | jed.cena/ Rate | ukupno /Amount
PREDMER I PREDRAČUN - faza I |  |  |  | BILL OF QUANTITIES AND COST ESTIMATE - Phase I
A. RADIJATORSKO GREJANJE |  |  |  | A. RADIATOR HEATING
| A1. GREJNA TELA I PRIBOR |  |  | A1. HEATING UNITS AND ACCESSORIES
1. | Nabavka i montaža čeličnih panelnih radijato- |  |  | 1. Purchase and installation of steel panel radiator units, product of 'JUGOTERM' or equivalent., with plugs and bleeder valves.
ra "JUGOTERM" ili slično komplet sa čepovima i
odzračnim slavinicama.
|  | 22-600/400 |  | 22-600/400 | kom./pcs | 9 |  | 0
|  | 22-600/600 |  | 22-600/600 | kom./pcs | 1 |  | 0
|  | 22-600/800 |  | 22-600/800 | kom./pcs | 1 |  | 0
|  | 22-600/1000 |  | 22-600/1000 | kom./pcs | 3 |  | 0
|  | 22-600/1200 |  | 22-600/1200 | kom./pcs | 2 |  | 0
|  | 33-900/1200 |  | 33-900/1200 | kom./pcs | 2 |  | 0
2. | Nabavka i montaža termoregulacionih glava |  |  | 2. Purchase and installation of thermostatic heads, product of 'Oventrop', or equivalent.
proizvod "Oventrop" ili slično.
| tip/type | Vindo TH |  | Vindo TH | kom./pcs | 18 |  | 0
3. | Nabavka i montaža radijatorskih ravnih ven- |  |  | 3. Purchase and installation of straight thermostatic radiator valves, with double regulation, product of 'Oventrop', or equivalent.
tila sa dvostrukom regulacijom proizvod
"Oventrop" ili slično.
| tip/type | AV6 | DN15 |  | kom./pcs | 18 |  | 0
4. | Nabavka i montaža radijatorskih ravnih zat- |  |  | 4. Purchase and installation of radiator lockshield valves, product of 'Oventrop', or equivalent.
varajućih navijaka proizvod "Oventrop" ili sl.
| tip/type | Combi 2 | DN15 |  | kom./pcs | 18 |  | 0
5. | Nabavka i montaža nosača za JUGOTERM |  |  | 5. Purchase and installation of JUGOTERM radiator carriers or equivalent..
radijatore ili slično.
[5 empty] | kompl./set | 18 |  | 0
6. | Izrada i montaža duplih veza za radijatore |  |  | 6. Fabrication and installation of double connection radiator fitting.
[5 empty] | kom./pcs | 18 |  | 0
| Ukupno A1: |  |  | Total A1: |  |  |  | 0
| A2. CEVNA MREŽA I PRIBOR |  |  | A2. PIPEWORK AND ACCESSORIES
1. | Nabavka i montaža crnih cevi za razvod tople |  |  | 1. Purchase and installation of hot and cold water black piping distribution network.
i hladne vode, JUS C.B5.221
| DN 15 | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 120 |  | 0
| DN 20 | f 26.9 x 2.3 |  | f 26.9 x 2.3 | m' | 96 |  | 0
| DN 25 | f 33.7 x 2.6 |  | f 33.7 x 2.6 | m' | 78 |  | 0
| DN 32 | f 42.4 x 2.9 |  | f 42.4 x 2.9 | m' | 146 |  | 0
| DN 40 | f 48.3 x 2.9 |  | f 48.3 x 2.9 | m' | 12 |  | 0
| DN 50 | f 60.3 x 2.9 |  | f 60.3 x 2.9 | m' | 42 |  | 0
2. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 2. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 | 0 | 0
| Ukupno A2: |  |  | Total A2: |  |  |  | 0
B. KLIMATIZACIJA |  |  |  | B. AIR-CONDITIONING
| B1. GREJNA/RASHLADNA TELA I PRIBOR |  |  | B1. HEATING/COOLING UNITS AND ACCESSORIES
2. | Nabavka i montaža ventilator konvektora (fan-coil |  |  | 2. Purchase and installation of ventilator convector (fan-coil) units for cassette installation. Product of 'DAIKIN', Japan or equivalent., mandatory with condensate pump and drain tray. Standard three-speed ventilator/ (winter/summer) switch room thermostat included. Fan coil unit fitted for two-pipe system. Four direction wind spliting casing included.
units) za kasetnu ugradnju. Proizvod "DAIKIN"
Yapan ili slično, obavezno sa pumpicom i tacnom za kondenzat.
U sklopu uređaja isporučuje se standardni sobni
termostat sa tri brzine rada ventilatora i preklopkom
zima/leto (žični). Fan coil uređaj je preipremljen
za dvocevno priključenje na instalaciju. Komplet sa
maskom sa četvorosmernim izduvavanjem.
| tip/type | FWF 02 |  | FWF 02 | kom./pcs | 31 |  | 0
| tip/type | FWF 03 |  | FWF 03 | kom./pcs | 16 |  | 0
| tip/type | FWF 04 |  | FWF 04 | kom./pcs | 4 |  | 0
| tip/type | FWC 07BT |  | FWC 07BT | kom./pcs | 58 |  | 0
| tip/type | FWC 08BT |  | FWC 08BT | kom./pcs | 21 |  | 0
| tip/type | FWC09BT |  | FWC09BT | kom./pcs | 48 |  | 0
3. | Nabavka i montaža ventilator konvektora (fan-coil |  |  | 3. Purchase and installation of ventilator convector (fan-coil) units for wall installation; Product of 'DAIKIN', Japan or equivalent., mandatory with condensate drain tray. Standard three-speed ventilator/ (winter/summer) switch room thermostat included. Fan coil unit fitted for two-pipe system.
units) za parapetnu ugradnju. Proizvod "DAIKIN"
Yapan ili slično, obavezno sa tacnom za kondenzat. U sklopu
uređaja (na uredjaju) isporučuje se standardni sobni
termostat sa tri brzine rada ventilatora i preklopkom
zima/leto. Fan coil uređaj je preipremljen
za dvocevno priključenje na instalaciju.
| tip/type | FW 04CT |  | FW 04CT | kom./pcs | 53 |  | 0
| tip/type | FW 06CT |  | FW 06CT | kom./pcs | 4 |  | 0
| tip/type | FW 08CT |  | FW 08CT | kom./pcs | 7 |  | 0
5. | Izrada i montaža duplih veza za fan coile. |  |  | 5. Fabrication and installation of double fan coil fittings. Fittings are fabricated from flexible heavy duty hoses and necessary shore accessories, of appropriate dimensions.
Veze se izrađuju od fleksibilnih pancirnih creva
i potrebnih fitinga za priključke odgovarajućih
dimenzija
|  | DN 15 / R 3/4" |  | DN 15 / R 3/4" | kompl./set | 31 |  | 0
|  | DN 20 / R 3/4" |  | DN 20 / R 3/4" | kompl./set | 84 |  | 0
|  | DN 25 / R 3/4" |  | DN 25 / R 3/4" | kompl./set | 127 |  | 0
6. | Nabavka i montaža kuglastih slavina sa |  |  | 6. Purchase and installation of ball valves with threaded fittings, NP6.
navojnim spojem NP6
|  | DN 20 |  | DN 20 | kom./pcs | 484 |  | 0
7. | Nabavka i montaža automatskih regulatora |  |  | 7. Purchase and installation of automatic flow control and balance valves, 'Oventrop' or equivalent, equipped with measuring components.
protoka I balans ventila "Oventrop" ili slično.
Komplet sa priključcima za merenje.
| tip Cocon QTZ |  | DN 15 ; 150-1050 l/h | DN 15 ; 150-1050 l/h | kom./pcs | 31 |  | 0
|  |  | DN 20 ; 180-1300 l/h | DN 20 ; 180-1300 l/h | kom./pcs | 84 |  | 0
|  |  | DN 25 ; 300-2000 l/h | DN 25 ; 300-2000 l/h | kom./pcs | 127 |  | 0
8. | Nabavka i montaža elektrotermičkog pogona za |  |  | 8. Purchase and installation of Cocon QTZ valves electrothermal actuator, 'Oventrop' or equivalent. For 220V, digital, 2 point, on/off.
Cocon QTZ ventile, "Oventrop" ili slično.
Za 220 V, digital, 2 tačkasto, on/off.
| tip/type | ET NC |  | ET NC | kom./pcs | 242 |  | 0
9. | Nabavka i montaža automatskih regulatora |  |  | 9. Purchase and installation of automatic flow control and balance valves, 'Oventrop' or equivalent; equipped with ventilation unit measuring components.
protoka I balans ventila "Oventrop" ili slično.
Komplet sa priključcima za merenje
za potrebe instalacije ventilacije - ventilac. Komora.
| tip Cocon QTZ |  | DN 25 ; 300-2000 l/h | DN 25 ; 300-2000 l/h | kom./pcs | 3 |  | 0
| tip Cocon QFC |  | DN 40 ; 0-6000 l/h | DN 40 ; 0-6000 l/h | kom./pcs | 1 |  | 0
10. | Nabavka i montaža elektromotornog pogona za |  |  | 10. Purchase and installation of Cocon Q valves electrothermal actuator, 'Oventrop' or equivalent. For 0-10V, analog, for networking of air-conditioning units.
Cocon Q ventile, "Oventrop" ili slično.
Za 0-10 V, analog, za potrebe povezivanja klima komora.
| tip/type | EM | kat.br. 1012700 |  | kom./pcs | 3 |  | 0
|  | EM | kat.br. 1158030 |  | kom./pcs | 1 |  | 0
11. | Nabavka i montaža pločastog izmenjivača toplote, komplet sa izolacijom proiozvod "DANFOSS" ili slično, sledećih tehničkih karakteristika: |  |  | 11. Purchase and installation of insulated panel heat exchanger, product of 'DANFOSS' or equivalent., following specifications:
| tip/type: | XGC-X026-L-4-P-177 D |  | XGC-X026-L-4-P-177 D
|  | - primar - glikol 30% ulaz/izlaz: 7/12 oC |  | - primary fluid - glycol 30% in/out: 7/12 oC
|  | - sekundar - voda ulaz/izlaz: 14/9 oC |  | - secondary fluid - water in/out: 14/9 oC
|  | - Q = 485 kW |  | - Q = 485 kW
|  | - priključci: DN100 NP25 |  | - fittings: DN100 NP25
|  | - Dp primar/sekundar: 36.17/19.3 kPa |  | - Dp primary/secondary: 36.17/19.3 kPa
|  | - š/d/v =450/1386/1261 |  | - w/l/h =450/1386/1261
|  | - masa: 674 kg |  | - weight: 674 kg
[5 empty] | kompl./set | 1 |  | 0
| tip/type: | XGC-X026-L-4-P-185 D |  | XGC-X026-L-4-P-185 D
|  | - primar - glikol 30% ulaz/izlaz: 7/12 oC |  | - primary fluid - glycol 30% in/out: 7/12 oC
|  | - sekundar - voda ulaz/izlaz: 14/9 oC |  | - secondary fluid - water in/out: 14/9 oC
|  | - Q = 538 kW |  | - Q = 538 kW
|  | - priključci: DN100 NP25 |  | - fittings: DN100 NP25
|  | - Dp primar/sekundar: 37.7/29.2 kPa |  | - Dp primary/secondary: 37.7/29.2 kPa
|  | - š/d/v =450/1386/1261 |  | - w/l/h =450/1386/1261
|  | - masa: 692 kg |  | - weight: 692 kg
[5 empty] | kompl./set | 1 |  | 0
12. | Nabavka i montaža gumenih kompezatora sa |  |  | 12. Purchase and installation of rubber flanged expansion joints for reducing vibration transmission, product of 'ELAFLEX', or equivalent.
sa prirubničkim spojem za smanjenje
prenošenja vibracija proizvod "ELAFLEX"
ili slično.
|  | DN 200 NP10 |  | DN 200 NP10 | kom./pcs | 4 |  | 0
13. | Nabavka i montaža kuglastih slavina |  |  | 13. Purchase and installation of ball valves with flanged fittings, NP10.
komplet sa prirubničkim spojem NP10.
| leptir | DN 150 |  | butterfly DN 150 | kom./pcs | 12 |  | 0
14. | Nabavka i montaža kuglastih slavina sa |  |  | 14. Purchase and installation of ball valves with threaded fittings, NP10
navojnim spojem NP10
|  | DN 25 |  | DN 25 | kom./pcs | 6 |  | 0
|  | DN 15 |  | DN 15 | kom./pcs | 2 |  | 0
15. | Izrada i montaža odzračnog suda |  |  | 15. Fabrication and installation of air exhaust vessel.
|  | f 219,1 x 5,9 x 250 mm |  | f 219,1 x 5,9 x 250 mm | kom./pcs | 2 |  | 0
16. | Nabavka i montaža rezervoara za ispuštanje |  |  | 16. Purchase and installation of ethylene-glycol discharge reservoir, volume 2000 lit.
etilen - glikola, zapremine 2000 litara.
[5 empty] | kom./pcs | 1 |  | 0
17. | Isporuka i montaža vazduhom hlađenog agregata - termo pumpe za spoljašnju montažu sa navojnim kompresorima proizvod "McQuay" -Italy ili ekvivalentno, koji radi u sistemu toplotne pumpe, u "standardnoj" izvedbi. Kompletno sa bakarnim cevima, izolacijom Armafleks, freonom HFC 134-a, sitnim potrošnim materijalom, elektro kablom za unutrašnje povezivanje. Uz agregat se isporučuje i pripadajući hidraulički modul (u okviru koga se isporučuje cirkulaciona pumpa za hladnu/toplu vodu odgovarajućeg kapaciteta, sigurnosni ventil, ventil za punjenje, ventil za pražnjenje, flow switch, sigurnosni elektro grejač isparivača i sva prateća merna, zaporna i sigurnosna armatura). Bez buffer tanka. |  |  | 17. Delivery and installation of air-ccoled chiller - outdoor installation thermal pump, with inverted driven screw compressors, product of ''McQuay", Italy or equivalent; operating in a heat pump system, standard. With copper piping, 'Armaflex' insulation, HFC 134 freon, supply material, electric cable for internal wiring. Chiller delivered with corresponding hydraulic module (including: cold/hot water circulation pump of appropriate capacity, afety valve, fill valve, discharge valve, flow switch, safety electric evaporator heater and all measuring, sealing and safety equipment). Without buffer tank.
| Komplet sa puštanjem u rad, garancijom. |  |  | With putting into operation, warranty.
| Montaža toplotnih pumpi je na krovu objekta |  |  | Heat pump installation is on building's roof (30m height).
visine 30 m.
| Standardna oprema: |  |  | Standard equipment:
| - grejač vodenog dela isparivača do -28oC |  |  | - water part evaporator heater up to -28oC
| - grejači ulja svakog kompresora |  |  | - oil heaters for each compressor
| - elektronski ekspanzioni ventili |  |  | - electronic expansion device
| - zaporni ventili na potisnoj i usisnoj strani kompresora |  |  | - discharge/suction line shut-off valves
| - manometar niskog pritiska |  |  | - low pressure side manometer
| - brojač radnih časova svakog kompresora |  |  | - hour run meter per compressor
| Dodatna oprema: |  |  | Additional equipment:
| - regulacija broja obrtaja ventilatora |  |  | - fan speed control device
| - flow switch |  |  | - flow switch
| - manometar niskog pritiska |  |  | - low pressure manometer
| - antivibracioni opružni oslonci |  |  | - antivibrational spring support
| - cirkulaciona puma |  |  | - circulation pump
| - ventil sigurnosti |  |  | - safety valve
| tip: McEnergy HPI Extension 144.3 |  |  | type: McEnergy HPI Extension 144.3
| * nominalni rashladni kapacitet 495 kW |  |  | * nominal cooling capacity 495 kW
| * boost rashladni kapacitet 603 kW |  |  | * boost cooling capacity 603 kW
| * nominalni grejni kapacitet 515 kW |  |  | * nominal heating capacity 515 kW
| * boost grejni kapacitet 657 kW |  |  | * boost heating capacity 657 kW
| * regulacija opterećenja 9-100% |  |  | * load control 9-100 %
| * Gradno = 5495 kg |  |  | * Gradno = 5495 kg
* pumpa tip/pump type: SPK 9 ; 114.2 kPa ; 91.9 m3/h ; 7.5 kW ; 3x400 V
[5 empty] | kompl./set | 1 |  | 0
| tip: McEnergy HPI Extension 153.3 |  |  | type: McEnergy HPI Extension 153.3
| * nominalni rashladni kapacitet 512 kW |  |  | * nominal cooling capacity 512 kW
| * boost rashladni kapacitet 636 kW |  |  | * boost cooling capacity 636 kW
| * nominalni grejni kapacitet 542 kW |  |  | * nominal heating capacity 542 kW
| * boost grejni kapacitet 710 kW |  |  | * boost heating capacity 710 kW
| * regulacija opterećenja 9-100% |  |  | * load control 9-100 %
| * Gradno = 5735 kg |  |  | * Gradno = 5735 kg
* pumpa tip/pump type: SPK 10 ; 117.2 kPa ; 96.07 m3/h ; 11 kW ; 3x400 V
[5 empty] | kompl./set | 1 |  | 0
| Ukupno B1: |  |  | Total B1: |  |  |  | 0
| B2. CEVNA MREŽA I PRIBOR |  |  | B2. PIPEWORK AND ACCESSORIES
1. | Nabavka i montaža crnih cevi za razvod tople |  |  | 1. Purchase and installation of hot and cold water black piping distribution network, JUS C.B5.221
i hladne vode, JUS C.B5.221
| DN 15 | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 760 |  | 0
| DN 20 | f 26.9 x 2.3 |  | f 26.9 x 2.3 | m' | 800 |  | 0
| DN 25 | f 33.7 x 2.6 |  | f 33.7 x 2.6 | m' | 900 |  | 0
| DN 32 | f 42.4 x 2.9 |  | f 42.4 x 2.9 | m' | 800 |  | 0
| DN 40 | f 48.3 x 2.9 |  | f 48.3 x 2.9 | m' | 500 |  | 0
| DN 50 | f 60.3 x 2.9 |  | f 60.3 x 2.9 | m' | 800 |  | 0
| DN 65 | f 76.1 x 2.9 |  | f 76.1 x 2.9 | m' | 300 |  | 0
| DN 80 | f 88.9 x 3.2 |  | f 88.9 x 3.2 | m' | 350 |  | 0
| DN 100 | f 114.3 x 3.6 |  | f 114.3 x 3.6 | m' | 280 |  | 0
| DN 125 | f 137.9 x 4.0 |  | f 137.9 x 4.0 | m' | 660 |  | 0
| DN 150 | f 168.3 x 4.5 |  | f 168.3 x 4.5 | m' | 170 |  | 0
2. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 2. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 | 0 | 0
3. | Nabavka i montaža krutih PVC |  |  | 3. Purchase and installation of stiff PVC piping for central condensate drain.
cevi za centralni odvod kondenzata
|  | f 32 |  | f 32 | m' | 1700 |  | 0
|  | f 40 |  | f 40 | m' | 200 |  | 0
|  | f 50 |  | f 50 | m' | 70 |  | 0
4. | Materijal za pričvršćivanje, spajanje i |  |  | 4. Fastening, joint and sealing supplies, PVC piping , elbows, T-profiles, etc., 40% from previous item unit rate.
dihtovanje PVC cevi kolena, račve i
slično, 40% od prethodne stavke.
[6 empty] | 0.4 | 0 | 0
5. | Nabavka i montaža zatvorene membranske |  |  | 5. Purchase and installation of (closed) membrane expansion vessel, 'ELBI' or equivalent.
ekspanzione posude "ELBI" ili slično:
| tip/type: | ERE-ERC 80 litara |  | ERE-ERC 80 lit
|  | - zapremina: 80 litara/10bar |  | - volume: 80 lit/10bar
|  | - priključak: DN25 |  | - fitting: DN25
[5 empty] | kom./pcs | 2 |  | 0
6. | Izrada i montaža odzračnog suda |  |  | 6. Fabrication and installation of air exhaust vessel.
|  | f 219,1 x 5,9 x 250 mm |  | f 219,1 x 5,9 x 250 mm | kom./pcs | 16 |  | 0
7. | Nabavka i montaža kuglastih slavina sa |  |  | 7. Purchase and installation of ball valves with thread fittings, NP 10
navojnim spojem NP10
|  | DN 15 |  | DN 15 | kom./pcs | 12 |  | 0
8. | Izrada i montaža konzola i nosača cevnog razvoda |  |  | 8. Fabrication and installation of consoles and piping network carriers, along profiled steel roof.
po krovu od profilisanog čelika
[5 empty] | kg. | 450 |  | 0
| Ukupno B2: |  |  | Total B2: |  |  |  | 0
C. PRIMARNA PODSTANICA |  |  |  | C. PRIMARY SUBSTATION
1. | Nabavka i montaža regulatora pritiska dimen- |  |  | 1. Purchase and installation of pressure control, DN 80, NP 25, product of 'DANFOSS' or equivalent.. Application up to 140 oC working water temperature.
zije DN 80, NP 25 proizvodnje "DANFOSS" ili slično.
Regulator je predviđen za vrelu vodu
radne temperature max. 140 °C,
| tip. VFG2 , Kvs = 80 m3/h. |  |  | type: VFG2 , Kvs = 80 m3/h.
[5 empty] | kom./pcs | 1 |  | 0
2. | Nabavka i montaža regulatora protoka dimen- |  |  | 2. Purchase and installation of flow control, DN 80, NP 25, product of 'DANFOSS' or equivalent.. Application up to 140 oC working water temperature.
zije DN 80, NP 25 proizvodnje "DANFOSS" ili slično
Regulator je predviđen za vrelu vodu
radne temperature max. 140 °C,
| tip. VFQ2 , Kvs = 80 m3/h. |  |  | type: VFQ2 , Kvs = 80 m3/h.
[5 empty] | kom./pcs | 1 |  | 0
3. | Nabavka i montaža ventila sigurnosti sa op- |  |  | 3. Purchase and installation of sping safety valve, dimensions DN, NP 16, product of 'DANFOSS' or equivalent., type SAID 25, maximum flow Qmax=4,5 m3/h, for pressures 3-11 bar. Application up to 140 oC water working temperature.
rugom dimenzije DN , NP 16 proizvodnje
"DANFOSS" ili slično, tip. SAID 25,
sa maximalnim protokom Qmax=4,5 m3/h,
za pritiske od 3-11 bar. Ventil je predviđen za
vrelu vodu radne temperature max. 140 °C,
[5 empty] | kom./pcs | 1 |  | 0
4. | Nabavka i montaža hvatača nečistoće, kom- |  |  | 4. Purchase and installation of impurity strainer, NP 16 flange included.
plet sa prirubničkim spojem NP 16
|  | DN 80 |  | DN 80 | kom./pcs | 1 |  | 0
5. | Nabavka i montaža odbojnog ventila NP 16 |  |  | 5. Purchase and installation of NP 16 repulsive valve.
|  | DN 80 |  | DN 80 | kom./pcs | 1 |  | 0
6. | Nabavka i montaža manometra f 160 mm, |  |  | 6. Purchase and installation of manometer, f 160 mm, measuring range:
mernog opsega:
|  | 0 - 16 bar |  | 0 - 16 bar | kom./pcs | 1 |  | 0
|  | 0 - 10 bar |  | 0 - 10 bar | kom./pcs | 3 |  | 0
7. | Nabavka i montaža živinog termometra u |  |  | 7. Purchase and installation of encapsulated mercury thermometer, straight, measuring range:
u čauri, ravnog, mernog opsega
|  | 0 - 200 °C |  | 0 - 200 °C | kom./pcs | 1 |  | 0
|  | 0 - 130 °C |  | 0 - 130 °C | kom./pcs | 1 |  | 0
8. | Nabavka i montaža crnih mufova |  |  | 8. Purchase and installation of black heat sleeves.
|  | DN 15 |  | DN 15 | kom./pcs | 6 |  | 0
9. | Izrada i montaža cevnih proširenja za mano- |  |  | 9. Fabrication and installation of pipe widenings (for manometers, thermometers, connections and collectors), in following sizes:
metre, termometre, priključenja i kolektore
sledećih dimemenzija:
|  | DN 125 / 1100 |  | DN 125 / 1100 | kom./pcs | 2 |  | 0
10. | Izrada i montaža konzola i nosača primarne |  |  | 10. Fabrication and installation of consoles and primary substation carriers, from profiled steel.
podstanice od proofilisanog čelika
[5 empty] | kg. | 50 |  | 0
11. | Nabavka i montaža crnih cevi za izradu pod- |  |  | 11. Purchase and installation of primary substation black piping, binding, welding supplies and other accessories inclusive.
stanice, zajedno sa spojnim, zavarnim i osta-
lim pomoćnim materijalom.
|  | DN 25 |  | DN 25 | m' | 9 |  | 0
|  | DN 80 |  | DN 80 | m' | 9 |  | 0
12. | Nabavka i montaža ultrazvučnog merača protoka |  |  | 12. Purchase and installation of ultrasonic thermal energy meter, Kamstrup or equivalent, type Multical 601-C, with flow meter, Ultraflow 65-R
Kamstrup ili slično tip Multical 601-C
sa meračem protoka Ultraflow 65-R
|  | DN 65 |  | DN 65 | m' | 1 |  | 0
13. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 13. Cleaning with a steel brush and double red lead coating of all primary substation piping.
ziranje svih cevnih elemenata podstanice
[5 empty] | m2 | 15 |  | 0
14. | Bojenje elemenata podstanice toplootpor- |  |  | 14. 2 layer coating of primary substation elements in thermal resistant green-yellow paint, CHROMOS -62 or equivalent; valve wheels to be coated in blue and red.
nom zeleno-žutom bojom CHROMOS -62 ili slično
u dva premaza, a točkove ventila plavom i
crvenom bojom.
[5 empty] | m2 | 25 |  | 0
15. | Izolacija cevnih elemenata primarne podsta- |  |  | 15. 4cm mineral wool insulation of primary substation piping, coated in Al-sheet metal.
nice, mineralnom vunom debljine 4 cm u
plaštu od Al-u lima
[5 empty] | m2 | 35 |  | 0
| Ukupno C: |  |  | Total C: |  |  |  | 0
D. SEKUNDARNA PODSTANICA |  |  |  | D. SECONDARY SUBSTATION
| D1. SEKUNDARNA PODSTANICA 1 |  |  | D1. SECONDARY SUBSTATION 1
1. | Nabavka i montaža pločastog izmenjivača toplote komplet sa izolacionom oblogom proiozvod "DANFOSS" ili slično, sledećih tehničkih karakteristika: |  |  | 1. Purchase and installation of insulated panel heat exchanger, product of 'DANFOSS' or equivalent, with following technical specifications:
| tip/type: | XB 70L-1 90 |  | XB 70L-1 90
|  | - primar ulaz/izlaz: 150/70 oC |  | - primary fluid in/out: 150/70 oC
|  | - sekundar ulaz/izlaz: 50/40 oC |  | - secondary fluid in/out: 50/40 oC
|  | - Q = 310 kW |  | - Q = 310 kW
|  | - priključci: DN65/100 NP25/NP6 |  | - fittings: DN65/100 NP25/NP6
|  | - Dp primar/sekundar: 1/19.8 kPa |  | - Dp primary/secondary: 1/19.8 kPa
|  | - š/d/v =365/190/1130 |  | - w/l/h =365/190/1130
|  | - masa: 175 kg |  | - weight: 175 kg
[5 empty] | kompl./set | 1 |  | 0
2. | Nabavka i montaža cirkulacionih pumpi |  |  | 2. Purchase and installation of 'Grundfos' or equivalent circulation pumps, with NP10 flanged fitting.
"Grundfos" ili slično komplet sa prirubničkim
spojem NP10.
| tip/type: | TPE 125-210/4-S |  | TPE 125-210/4-S
|  | - protok: 83.37 m3/h |  | - flow: 83.37 m3/h
|  | - napor: 146.816 kPa |  | - pressure: 146.816 kPa
|  | - snaga: 11 kW, 3x400 V |  | - power: 11 kW, 3x400 V
[5 empty] | kom./pcs | 1 |  | 0
3. | Nabavka i montaža gumenih kompezatora sa |  |  | 3. Purchase and installation of rubber flanged expansion joints for reducing vibration transmission, product of 'ELAFLEX', or equivalent.
sa prirubničkim spojem za smanjenje
prenošenja vibracija proizvod "ELAFLEX"
ili slično.
|  | DN 150 NP10 |  | DN 150 NP10 | kom./pcs | 2 |  | 0
4. | Nabavka i montaža zatvorene membranske |  |  | 4. Purchase and installation of (closed) membrane expansion vessel, 'ELBI' or equivalent.
ekspanzione posude "ELBI" ili slično:
| tip/type: | ERE-ERC 500 litara |  | ERE-ERC 500 lit
|  | - zapremina: 500 litara/10bar |  | - volume: 500 lit/10bar
|  | - priključak: DN32 |  | - fitting: DN32
[5 empty] | kom./pcs | 1 |  | 0
5. | Nabavka i montaža ventila sigurnosti sa |  |  | 5. Purchase and installation of spring safety valves, 'Prescor' or equivalent.
oprugom, "Prescor" ili slično:
|  | DN32 NP10 |  | DN32 NP10 | kom./pcs | 1 |  | 0
6. | Nabavka i montaža kuglastih slavina sa |  |  | 6. Purchase and installation of ball valves with thread fitting
navojnim spojem
| NP10 | DN 15 |  | NP10 DN 15 | kom./pcs | 6 |  | 0
|  | DN 20 |  | DN 20 | kom./pcs | 2 |  | 0
|  | DN 25 |  | DN 25 | kom./pcs | 2 |  | 0
|  | DN 32 |  | DN 32 | kom./pcs | 2 |  | 0
|  | DN 100 |  | DN 100 | kom./pcs | 2 |  | 0
|  | DN 125 |  | DN 125 | kom./pcs | 2 |  | 0
| NP16 | DN 15 |  | NP16 DN 15 | kom./pcs | 2 |  | 0
|  | DN 25 |  | DN 25 | kom./pcs | 1 |  | 0
|  | DN 32 |  | DN 32 | kom./pcs | 2 |  | 0
7. | Nabavka i montaža leptirstih slavina |  |  | 7. Purchase and installation of butterly valves with flanged fittings.
komplet sa prirubničkim spojem
| NP10 | DN 150 |  | NP10 DN 150 | kom./pcs | 4 |  | 0
8. | Nabavka i montaža leptirste prigušnice |  |  | 8. Purchase and installation of butterfly damper with flanged NP16 fittings.
komplet sa prirubničkim spojem NP16.
|  | DN 32 |  | DN 32 | kom./pcs | 1 |  | 0
9. | Nabavka i montaža nepovratnog ventila |  |  | 9. Purchase and installation of irreversible valve, with flanged NP16 fitting.
komplet sa prirubničkim spojem NP16
|  | DN 25 |  | DN 25 | kom./pcs | 1 |  | 0
10. | Nabavka i montaža automatskih regulatora |  |  | 10. Purchase and installation of automatic flow control and balance valves, 'Oventrop' or equivalent.
protoka I balans ventila "Oventrop" ili slično.
| tip/type: Cocon QTZ |  | DN 32 ; 600-3600 l/h | DN 32 ; 600-3600 l/h | kom./pcs | 1 |  | 0
11. | Nabavka i montaža hvatača nečistoće |  |  | 11. Purchase and installation of impurity strainer, NP 10 flange included.
komplet sa prirubničkim spojem NP10
| NP10 | DN 150 |  | NP10 DN 150 | kom./pcs | 1 |  | 0
| NP16 | DN 32 |  | NP16 DN 32 | kom./pcs | 1 |  | 0
12. | Nabavka i montaža manometra f100, sa trokrakom |  |  | 12. Purchase and installation of f100 manometer with DN15 three-way tap; measuring range 0-6 bar.
manometarskom slavinicom DN15, mernog opsega 0-6 bar.
[5 empty] | kom./pcs | 3 |  | 0
13. | Izrada i montaža odzračnog suda |  |  | 13. Fabrication and installation of air exhaust vessel.
|  | f 168,3 x 4,5 x 200 mm |  | f 168,3 x 4,5 x 200 mm | kom./pcs | 2 |  | 0
14. | Nabavka i montaža živinog termometra u metalnoj |  |  | 14. Purchase and installation of metal encapsulated mercury thermometer, straight, measuring range 0-130 oC
čauri, ravnog, mernog opsega 0-130 °C
[5 empty] | kom./pcs | 2 |  | 0
15. | Nabavka i montaža crnih mufova |  |  | 15. Purchase and installation of black heat sleeves.
|  | DN 15 |  |  | kom./pcs | 3 |  | 0
16. | Izrada i montaža razdelnika i sabirnika, |  |  | 16. Fabrication and installation of splitter/collector, insulated with 'Armaflex-AC' or equivalent.
komplet izolovani izolacijom "Armaflex-AC"
ili slično.
| f 323,9 x 7,1 x 1100 mm |  |  | f 323,9 x 7,1 x 1100 mm
| - priključci : DN100x2; DN125X1; |  |  | - fittings: DN100x2; DN125X1;
[5 empty] | kompl./set | 2 |  | 0
17. | Nabavka i montaža crnih cevi za izradu |  |  | 17. Purchase and installation of secondary substation black piping.
sekundarne podstanice
| DN15 | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 36 |  | 0
| DN25 | f 33.7 x 2.6 |  | f 33.7 x 2.6 | m' | 3 |  | 0
| DN32 | f 42.4 x 2.9 |  | f 42.4 x 2.9 | m' | 30 |  | 0
| DN100 | f 114.3 x 3.6 |  | f 114.3 x 3.6 | m' | 6 |  | 0
| DN125 | f 137.9 x 4.0 |  | f 137.9 x 4.0 | m' | 6 |  | 0
| DN150 | f 168.3 x 4.5 |  | f 168.3 x 4.5 | m' | 12 |  | 0
18. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 18. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 |  | 0
19. | Nabavka i montaža automatike za vođenje procesa |  |  | 19. Purchase and installation of heating automation system, which includes:
grejanja, koja u svom kompletu sadrži:
| - senzor SPOLJNE temperature vazduha "SIEMENS" ili slično |  |  | - EXTERNAL air temperature sensor, produc of "SIEMENS" or equivalent
[5 empty] | kom./pcs | 1 |  | 0
| - senzor temperature vode "SIEMENS" ili slično |  |  | - water temperature sensor, product of "SIEMENS" or equivalent
|  | tip QAE2120.010 |  | type QAE2120.010 | kom./pcs | 1 |  | 0
| - prolazni regulacioni ventil "Siemens" ili slično |  |  | - passage regulation valve, product of "Siemens" or equivalent, with ALG 323 threaded fitting
komplet sa navojnim spojem ALG 323
|  | VVG41.25, DN 25, kvs=10 m3/h |  | VVG41.25, DN 25, kvs=10 m3/h | kom./pcs | 1 |  | 0
| - trokraki regulacioni ventil "Siemens" ili slično |  |  | - three way regulation valve, product of "Siemens" or equivalent, with flanged fitting
komplet sa prirubničkim spojem
|  | VXF31.91 DN 125, kvs=200 m3/h |  | VXF31.91 DN 125, kvs=200 m3/h | kom./pcs | 2 |  | 0
| - elektromotorni pogon. 1x230 V |  |  | - electromotor. 1x230 V
|  | SQX32.00 |  | SQX32.00 | kom./pcs | 1 |  | 0
|  | SKC32.60 |  | SKC32.60 | kom./pcs | 2 |  | 0
| sve naregulisano i pušteno u rad. |  |  | fine-tuned and put into operation.
20. | Izrada i montaža konzola i nosača podstanice |  |  | 20. Purchase and installation of consoles and substation carriers, fabricated from profiled steel.
od profilisanog čelika
[5 empty] | kg. | 500 |  | 0
21. | Izrada betonskog temeljnog bloka |  |  | 21. Fabrication of concrete foundation block, size 750x750x350 mm. Top surface with anchoring for circulation pump steel platform, weight 350kg. Concrete block mounted on four anti vibration spirng mounts.
dim 750x750x350 mm. Sa gornje strane
bloka ostavljaju se odgovarajući ankeri
za postavljanje čelične platforme za nošenje
cirkulacione pumpe, težine 350kg. Sa donje
strane betonskog bloka postavljaju se
četiri antivibraciona opružna oslonca.
[5 empty] | kompl./set | 1 |  | 0
22. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 22. Cleaning with a steel brush and double red lead coating of all substation piping.
ziranje svih cevnih elemenata podstanice
[5 empty] | m2 | 18 |  | 0
23. | Izolacija cevnih elemenata sekundarne podsta- |  |  | 23. 4cm mineral wool insulation of primary substation piping, coated in Al-sheet metal, or equivalent.
nice za grejanje, mineralnom vunom debljine 4 cm u
plaštu od Al-u lima ili slično.
[5 empty] | m2 | 13 |  | 0
24. | Izolacija cevnog razvoda hladne vode prefabrikovanom izolacijom "Armaflex-AF" ili slično tip AF-4 ili slično po metru dužine cevi. |  |  | 24. Cold water piping insulation, from prefabricated 'Armaflex-AC' or equivalent, per m' of piping.
| f 114.1 x 3.6 |  | AF-4-114 | AF-4-114 (23,5 mm) | m' | 12 |  | 0
| f 139.7 x 4.0 |  | AF-4-140 | AF-4-140 (24,5 mm) | m' | 6 |  | 0
| f 168.3 x 4.5 |  | AF-4-168 | AF-4-168 (25 mm) | m' | 12 |  | 0
| Ukupno D1: |  |  | Total D1: |  |  |  | 0
| D2. SEKUNDARNA PODSTANICA 5 |  |  | D2. SECONDARY SUBSTATION 5
1. | Nabavka i montaža pločastog izmenjivača toplote komplet sa izolacionom oblogom proiozvod "DANFOSS" ili slično, sledećih tehničkih karakteristika: |  |  | 1. Purchase and installation of insulated panel heat exchanger, product of 'DANFOSS' or equivalent, with following specifications:
| tip/type: | XB 70L-1 120 |  | XB 70L-1 120
|  | - primar ulaz/izlaz: 150/70 oC |  | - primary fluid in/out: 150/70 oC
|  | - sekundar ulaz/izlaz: 50/40 oC |  | - secondary fluid in/out: 50/40 oC
|  | - Q = 400 kW |  | - Q = 400 kW
|  | - priključci: DN65/100 NP25/NP6 |  | - fittings: DN65/100 NP25/NP6
|  | - Dp primar/sekundar: 1/18.8 kPa |  | - Dp primary/secondary: 1/18.8 kPa
|  | - š/d/v =450/250/1130 |  | - w/l/h =450/250/1130
|  | - masa: 220 kg |  | -weight: 220 kg
[5 empty] | kompl./set | 1 |  | 0
2. | Nabavka i montaža cirkulacionih pumpi |  |  | 2. Purchase and installation of 'Grundfos' or equivalentcirculation pumps, with NP10 flanged fitting.
"Grundfos" ili slično komplet sa prirubničkim
spojem NP10.
| tip/type: | TPE 125-210/4-S |  | TPE 125-210/4-S
|  | - protok: 87.19 m3/h |  | - flow: 87.19 m3/h
|  | - napor: 155 kPa |  | - pressure: 155 kPa
|  | - snaga: 11 kW, 3x400 V |  | - power: 11 kW, 3x400 V
[5 empty] | kom./pcs | 1 |  | 0
3. | Nabavka i montaža gumenih kompezatora sa |  |  | 3. Purchase and installation of rubber flanged expansion joints for reducing vibration transmission, product of 'ELAFLEX', or equivalent.
sa prirubničkim spojem za smanjenje
prenošenja vibracija proizvod "ELAFLEX"
ili slično.
|  | DN 150 NP10 |  | DN 150 NP10 | kom./pcs | 2 |  | 0
4. | Nabavka i montaža zatvorene membranske |  |  | 4. Purchase and installation of (closed) membrane expansion vessel, 'ELBI' or equivalent.
ekspanzione posude "ELBI" ili slično:
| tip/type: | ERE-ERC 500 litara |  | ERE-ERC 500 lit
|  | - zapremina: 500 litara/10bar |  | - volume: 500 lit/10bar
|  | - priključak: DN32 |  | - fitting: DN32
[5 empty] | kom./pcs | 1 |  | 0
5. | Nabavka i montaža ventila sigurnosti sa |  |  | 5. Purchase and installation of spring safety valves, 'Prescor' or equivalent.
oprugom, "Prescor" ili slično:
|  | DN25 NP10 |  | DN25 NP10 | kom./pcs | 1 |  | 0
6. | Nabavka i montaža kuglastih slavina sa |  |  | 6. Purchase and installation of ball valves with thread fitting.
navojnim spojem
| NP10 | DN 15 |  | NP10 DN 15 | kom./pcs | 8 |  | 0
|  | DN 25 |  | DN 25 | kom./pcs | 2 |  | 0
|  | DN 32 |  | DN 32 | kom./pcs | 2 |  | 0
|  | DN 100 |  | DN 100 | kom./pcs | 8 |  | 0
|  | DN 125 |  | DN 125 | kom./pcs | 2 |  | 0
| NP16 | DN 25 |  | NP16 DN 25 | kom./pcs | 3 |  | 0
|  | DN 40 |  | DN 40 | kom./pcs | 2 |  | 0
7. | Nabavka i montaža leptirstih slavina |  |  | 7. Purchase and installation of butterly valves with flanged fittings.
komplet sa prirubničkim spojem
| NP10 | DN 150 |  | NP10 DN 150 | kom./pcs | 4 |  | 0
8. | Nabavka i montaža leptirste prigušnice |  |  | 8. Purchase and installation of butterfly damper with flanged NP16 fittings.
komplet sa prirubničkim spojem NP16.
|  | DN 40 |  | DN 40 | kom./pcs | 1 |  | 0
9. | Nabavka i montaža nepovratnog ventila |  |  | 9. Purchase and installation of irreversible valve, with flanged NP16 fitting.
komplet sa prirubničkim spojem NP16
|  | DN 25 |  | DN 25 | kom./pcs | 1 |  | 0
10. | Nabavka i montaža automatskih regulatora |  |  | 10. Purchase and installation of automatic flow control and balance valves, 'Oventrop' or equivalent.
protoka I balans ventila "Oventrop" ili slično.
| tip/type: Cocon QTZ |  | DN 32 ; 600-3600 l/h | DN 32 ; 600-3600 l/h | kom./pcs | 1 |  | 0
11. | Nabavka i montaža hvatača nečistoće |  |  | 11. Purchase and installation of impurity strainer, NP 10 flange included.
komplet sa prirubničkim spojem NP10
| NP10 | DN 150 |  | NP10 DN 150 | kom./pcs | 1 |  | 0
| NP16 | DN 40 |  | NP16 DN 40 | kom./pcs | 1 |  | 0
12. | Nabavka i montaža manometra f100, sa trokrakom |  |  | 12. Purchase and installation of f100 manometer with DN15 three-way tap; measuring range 0-6 bar.
manometarskom slavinicom DN15, mernog opsega 0-6 bar.
[5 empty] | kom./pcs | 4 |  | 0
13. | Izrada i montaža odzračnog suda |  |  | 13. Fabrication and installation of air exhaust vessel.
|  | f 168,3 x 4,5 x 200 mm |  | f 168,3 x 4,5 x 200 mm | kom./pcs | 8 |  | 0
14. | Nabavka i montaža živinog termometra u metalnoj |  |  | 14. Purchase and installation of metal encapsulated mercury thermometer, straight, measuring range 0-130 oC.
čauri, ravnog, mernog opsega 0-130 °C
[5 empty] | kom./pcs | 8 |  | 0
15. | Nabavka i montaža crnih mufova |  |  | 15. Purchase and installation of black heat sleeves.
|  | DN 15 |  | DN 15 | kom./pcs | 12 |  | 0
16. | Izrada i montaža razdelnika i sabirnika, |  |  | 16. Fabrication and installation of splitter/collector, insulated with 'Armaflex-AC' or equivalent.
komplet izolovani izolacijom "Armaflex-AC"
ili slično.
| f 323,9 x 7,1 x 1550 mm |  |  | f 323,9 x 7,1 x 1550 mm
| - priključci : DN125x1;DN100x3; |  |  | - fittings : DN125x1;DN100x3; | kompl./set | 2 |  | 0
17. | Nabavka i montaža crnih cevi za izradu |  |  | 17. Purchase and installation of secondary substation black piping.
sekundarne podstanice
| DN15 | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 54 |  | 0
| DN40 | f 48.3 x 2.9 |  | f 48.3 x 2.9 | m' | 56 |  | 0
| DN100 | f 114.3 x 3.6 |  | f 114.3 x 3.6 | m' | 18 |  | 0
| DN125 | f 137.9 x 4.0 |  | f 137.9 x 4.0 | m' | 6 |  | 0
| DN150 | f 168.3 x 4.5 |  | f 168.3 x 4.5 | m' | 12 |  | 0
18. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 18. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 | 0 | 0
19. | Nabavka i montaža automatike za vođenje procesa |  |  | 19. Purchase and installation of heating automation system, including:
grejanja, koja u svom kompletu sadrži:
| - senzor temperature vode "SIEMENS" ili slično |  |  | - water temperature sensor, product of "SIEMENS" or equivalent
|  | tip QAE2120.010 |  | type QAE2120.010 | kom./pcs | 1 |  | 0
| - prolazni regulacioni ventil "Siemens" ili slično |  |  | - passage regulation valve, product of "Siemens" or equivalent, with ALG 323 threaded fitting
komplet sa navojnim spojem ALG 323
|  | VVG41.32, DN 32, kvs=10 m3/h |  | VVG41.32, DN 32, kvs=10 m3/h | kom./pcs | 1 |  | 0
| - trokraki regulacioni ventil "Siemens" ili slično |  |  | - three way regulation valve, product of "Siemens" or equivalent, with flanged fitting
komplet sa prirubničkim spojem
|  | VXF31.91 DN 125, kvs=200 m3/h |  | VXF31.91 DN 125, kvs=200 m3/h | kom./pcs | 2 |  | 0
| - elektromotorni pogon. 1x230 V |  |  | - electromotor. 1x230 V
|  | SQX32.00 |  | SQX32.00 | kom./pcs | 1 |  | 0
|  | SKC32.60 |  | SKC32.60 | kom./pcs | 2 |  | 0
| sve naregulisano i pušteno u rad. |  |  | fine-tuned and put into operation.
20. | Izrada i montaža konzola i nosača podstanice |  |  | 20. Purchase and installation of consoles and substation carriers, fabricated from profiled steel.
od profilisanog čelika
[5 empty] | kg. | 500 |  | 0
21. | Izrada betonskog temeljnog bloka |  |  | 21. Fabrication of concrete foundation block, size 750x750x350 mm. Top surface with anchoring for circulation pump steel platform, weight 350kg. Concrete block mounted on four anti vibration spirng mounts.
dim 750x750x350 mm. Sa gornje strane
bloka ostavljaju se odgovarajući ankeri
za postavljanje čelične platforme za nošenje
cirkulacione pumpe, težine 350kg. Sa donje
strane betonskog bloka postavljaju se
četiri antivibraciona opružna oslonca.
[5 empty] | kompl./set | 1 |  | 0
22. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 22. Cleaning with a steel brush and double red lead coating of all substation piping.
ziranje svih cevnih elemenata podstanice
[5 empty] | m2 | 28 |  | 0
23. | Izolacija cevnih elemenata sekundarne podsta- |  |  | 23. 4cm mineral wool insulation of primary substation piping, coated in Al-sheet metal, or equivalent.
nice za grejanje, mineralnom vunom debljine 4 cm u
plaštu od Al-u lima ili slično.
[5 empty] | m2 | 22 |  | 0
24. | Izolacija cevnog razvoda hladne vode prefabrikovanom izolacijom "Armaflex-AF" tip AF-4 ili slično po metru dužine cevi. |  |  | 24. Cold water piping insulation, from prefabricated 'Armaflex-AC' type AF-4 or equivalent, per m' of piping.
| f 114.1 x 3.6 |  | AF-4-114 | AF-4-114 (23,5 mm) | m' | 18 |  | 0
| f 139.7 x 4.0 |  | AF-4-140 | AF-4-140 (24,5 mm) | m' | 6 |  | 0
| f 168.3 x 4.5 |  | AF-4-168 | AF-4-168 (25 mm) | m' | 12 |  | 0
| Ukupno D2: |  |  | Total D2: |  |  |  | 0
| D3. SEKUNDARNA PODSTANICA 8 |  |  | D3. SECONDARY SUBSTATION 8
1. | Nabavka i montaža cirkulacionih pumpi |  |  | 1. Purchase and installation of 'Grundfos' or equivalent circulation pumps, with NP10 threaded fitting.
"Grundfos" ili slično komplet sa navojnim spojem NP10.
| tip/type: | UPS 25-60 180 |  | UPS 25-60 180
|  | - protok: 0.55 m3/h |  | - flow: 0.55 m3/h
|  | - napor: 20.943 kPa |  | - pressure: 20.943 kPa
|  | - snaga: 90 W, 1x230 V |  | - power: 90 W, 1x230 V
[5 empty] | kom./pcs | 1 |  | 0
2. | Nabavka i montaža kuglastih slavina sa |  |  | 2. Purchase and installation of ball valves with thread fitting
navojnim spojem
| NP 10 | DN 25 |  | NP 10 DN 25 | kom./pcs | 2 |  | 0
| NP 16 | DN 15 |  | NP 16 DN 15 | kom./pcs | 2 |  | 0
|  | DN 20 |  | DN 20 | kom./pcs | 1 |  | 0
3. | Nabavka i montaža leptirste prigušnice |  |  | 3. Purchase and installation of butterfly damper with flanged NP16 fittings.
komplet sa prirubničkim spojem NP16.
|  | DN 15 |  | DN 15 | kom./pcs | 1 |  | 0
4. | Nabavka i montaža hvatača nečistoće |  |  | 4. Purchase and installation of impurity strainer, NP 16 flange included.
komplet sa prirubničkim spojem NP16
|  | DN 15 |  | DN 15 | kom./pcs | 1 |  | 0
5. | Nabavka i montaža manometra f100, sa trokrakom |  |  | 5. Purchase and installation of f100 manometer with DN15 three-way tap; measuring range 0-6 bar.
manometarskom slavinicom DN15, mernog opsega 0-6 bar.
[5 empty] | kom./pcs | 1 |  | 0
6. | Nabavka i montaža živinog termometra u metalnoj |  |  | 6. Purchase and installation of metal encapsulated mercury thermometer, straight, measuring range 0-130 oC.
čauri, ravnog, mernog opsega 0-130 °C
[5 empty] | kom./pcs | 1 |  | 0
7. | Nabavka i montaža crnih mufova |  |  | 7. Purchase and installation of black heat sleeves.
|  | DN 15 |  | DN 15 | kom./pcs | 2 |  | 0
8. | Nabavka i montaža crnih cevi za izradu |  |  | 8. Purchase and installation of secondary substation black piping.
sekundarne podstanice
|  | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 36 |  | 0
|  | f 33.7 x 2.6 |  | f 33.7 x 2.6 | m' | 12 |  | 0
9. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 9. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 | 0 | 0
10. | Izrada i montaža proširenja za termometre, |  |  | 10. Fabrication and installation of pipe widenings for manometers, thermometers, etc.
manometre i sl.
| f 60,3 x 2,9 x 200 mm |  |  | f 60,3 x 2,9 x 200 mm | kom./pcs | 1 |  | 0
| f 60,3 x 2,9 x 250 mm |  |  | f 60,3 x 2,9 x 250 mm | kom./pcs | 1 |  | 0
11. | Nabavka i montaža automatike za vođenje procesa |  |  | 11. Purchase and installation of heating automation system, including:
grejanja, koja u svom kompletu sadrži:
| - zaštitni termostat "SIEMENS" ili slično |  |  | - safety thermostate, "SIEMENS" or equivalent
|  | tip RAK-TW1000 |  | type RAK-TW1000 | kom./pcs | 1 |  | 0
| - senzor temperature vode "SIEMENS" ili slično |  |  | - water temperature sensor, product of "SIEMENS" or equivalent
|  | tip QAE2120.010 |  | type QAE2120.010 | kom./pcs | 1 |  | 0
| - prolazni regulacioni ventil "Siemens" ili slično |  |  | - passage regulation valve, product of "Siemens" or equivalent, with ALG 323 threaded fitting
komplet sa navojnim spojem ALG 323
|  | VVG41.11, DN 15, kvs=2.5 m3/h |  | VVG41.11, DN 15, kvs=2.5 m3/h | kom./pcs | 1 |  | 0
| - elektromotorni pogon. 1x230 V |  |  | - electromotor. 1x230 V
|  | SQX32.00 |  | SQX32.00 | kom./pcs | 1 |  | 0
| sve naregulisano i pušteno u rad. |  |  | fine-tuned and put into operation.
12. | Izrada i montaža konzola i nosača podstanice |  |  | 12. Purchase and installation of consoles and substation carriers, fabricated from profiled steel.
od profilisanog čelika
[5 empty] | kg. | 25 |  | 0
13. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 13. Cleaning with a steel brush and double red lead coating of all substation piping.
ziranje svih cevnih elemenata podstanice
[5 empty] | m2 | 4 |  | 0
14. | Izolacija cevnih elemenata sekundarne podsta- |  |  | 14. 4cm mineral wool insulation of primary substation piping, coated in Al-sheet metal, or equivalent.
nice za grejanje, mineralnom vunom debljine 4 cm u
plaštu od Al-u lima ili slično.
[5 empty] | m2 | 15 |  | 0
| Ukupno D3: |  |  | Total D3: |  |  |  | 0
| D4. SEKUNDARNA PODSTANICA 9 |  |  | D4. SECONDARY SUBSTATION 9
1. | Nabavka i montaža cirkulacionih pumpi |  |  | 1. Purchase and installation of 'Grundfos' circulation pumps, with NP10 threaded fitting or equivalent.
"Grundfos" komplet sa navojnim spojem NP10
ili slično.
| tip/type: | UPE 32-60 180 |  | UPE 32-60 180
|  | - protok: 2.89 m3/h |  | - flow: 2.89 m3/h
|  | - napor: 18.519 kPa |  | - pressure: 18.519 kPa
|  | - snaga: 40-100 W, 1x230 V |  | - power: 40-100 W, 1x230 V
[5 empty] | kom./pcs | 1 |  | 0
2. | Nabavka i montaža kuglastih slavina sa |  |  | 2. Purchase and installation of ball valves with thread fitting
navojnim spojem
| NP10 | DN 15 |  | NP10 DN 15 | kom./pcs | 5 |  | 0
|  | DN 50 |  | DN 50 | kom./pcs | 2 |  | 0
3. | Nabavka i montaža leptirste prigušnice |  |  | 3. Purchase and installation of butterfly damper with flanged NP16 fittings.
komplet sa prirubničkim spojem NP16.
|  | DN 15 |  | DN 15 | kom./pcs | 1 |  | 0
4. | Nabavka i montaža hvatača nečistoće |  |  | 4. Purchase and installation of impurity strainer, NP 16 flange included.
komplet sa prirubničkim spojem NP16
|  | DN 15 |  | DN 15 | kom./pcs | 1 |  | 0
5. | Nabavka i montaža manometra f100, sa trokrakom |  |  | 5. Purchase and installation of f100 manometer with DN15 three-way tap; measuring range 0-6 bar.
manometarskom slavinicom DN15, mernog opsega 0-6 bar.
[5 empty] | kom./pcs | 1 |  | 0
6. | Nabavka i montaža živinog termometra u metalnoj |  |  | 6. Purchase and installation of metal encapsulated mercury thermometer, straight, measuring range 0-130 oC.
čauri, ravnog, mernog opsega 0-130 °C
[5 empty] | kom./pcs | 1 |  | 0
7. | Nabavka i montaža crnih mufova |  |  | 7. Purchase and installation of black heat sleeves.
|  | DN 15 |  | DN 15 | kom./pcs | 2 |  | 0
8. | Izrada i montaža odzračnog suda |  |  | 8. Fabrication and installation of air exhaust vessel.
|  | f 168,3 x 4,5 x 100 mm |  | f 168,3 x 4,5 x 100 mm | kom./pcs | 2 |  | 0
9. | Nabavka i montaža crnih cevi za izradu |  |  | 9. Purchase and installation of secondary substation black piping.
sekundarne podstanice
|  | f 21.3 x 2.0 |  | f 21.3 x 2.0 | m' | 90 |  | 0
|  | f 60.3 x 2.9 |  | f 60.3 x 2.9 | m' | 12 |  | 0
10. | Spojni, zavarni i ostali pomoćni materijal, |  |  | 10. Binding, welding and other auxiliary supplies, pipe bends, oxygen, acetylene, hangers etc., 50% from previous item unit rate.
cevni lukovi, kiseonik, disugas, večaljke i
slično, 50% od prethodne stavke
[6 empty] | 0.5 | 0 | 0
11. | Nabavka i montaža automatike za vođenje procesa |  |  | 11. Purchase and installation of heating automation system, including:
grejanja, koja u svom kompletu sadrži:
| - zaštitni termostat "SIEMENS" ili slično |  |  | - safety thermostate, "SIEMENS" or equivalent
|  | tip RAK-TW1000 |  | type RAK-TW1000 | kom./pcs | 1 |  | 0
| - senzor temperature vode "SIEMENS" ili slično |  |  | - water temperature sensor, product of "SIEMENS" or equivalent
|  | tip QAE2120.010 |  | type QAE2120.010 | kom./pcs | 1 |  | 0
| - prolazni regulacioni ventil "Siemens" ili slično |  |  | - passage regulation valve, product of "Siemens" or equivalent, with ALG 323 threaded fitting
komplet sa navojnim spojem ALG 323
|  | VVG41.14, DN 15, kvs=1.6 m3/h |  | VVG41.14, DN 15, kvs=1.6 m3/h | kom./pcs | 1 |  | 0
| - elektromotorni pogon. 1x230 V |  |  | - electromotor. 1x230 V
|  | SQX32.00 |  | SQX32.00 | kom./pcs | 1 |  | 0
| sve naregulisano i pušteno u rad. |  |  | fine-tuned and put into operation.
12. | Izrada i montaža konzola i nosača podstanice |  |  | 12. Purchase and installation of consoles and substation carriers, fabricated from profiled steel.
od profilisanog čelika
[5 empty] | kg. | 25 |  | 0
13. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 13. Cleaning with a steel brush and double red lead coating of all substation piping.
ziranje svih cevnih elemenata podstanice
[5 empty] | m2 | 8.1 |  | 0
14. | Izolacija cevnih elemenata sekundarne podsta- |  |  | 14. 4cm mineral wool insulation of primary substation piping, coated in Al-sheet metal, or equivalent.
nice za grejanje, mineralnom vunom debljine 4 cm u
plaštu od Al-u lima ili slično.
[5 empty] | m2 | 30 |  | 0
| Ukupno D4: |  |  | Total D4: |  |  |  | 0
| E. OSTALI RADOVI |  |  | E. OTHER WORKS
1. | Izolacija cevnog razvoda radijatorskog grejanja |  |  | 1. Insulation of piping distribution network, with prebaricated 'Armaflex' insulation, or equivalent, per m' of piping, 9 mm.
prefabrikovanom izolacijom "Armaflex" ili slično
po metru dužine cevi, 9mm.
| f 21.3 x 2.0 |  | TL-22/9 | TL-22/9 | m' | 120 |  | 0
| f 26.9 x 2.3 |  | TL-28/9 | TL-28/9 | m' | 96 |  | 0
| f 33.7 x 2.6 |  | TL-35/9 | TL-35/9 | m' | 78 |  | 0
| f 42.4 x 2.9 |  | TL-42/9 | TL-42/9 | m' | 146 |  | 0
| f 48.3 x 2.9 |  | TL-48/9 | TL-48/9 | m' | 12 |  | 0
| f 60.3 x 2.9 |  | TL-60/9 | TL-60/9 | m' | 42 |  | 0
2. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 2. Cleaning with a steel brush and double red lead coating of all floor and radiator heating piping.
ziranje celokupne cevne mreže podnog i
radijatorskog grejanja
[5 empty] | m2 | 122 |  | 0
3. | Bojenje vidljive cevne mreže podnog i radijatorskog grejanja belim radijator lakom u dva premaza. |  |  | 3. Coating of exposed floor and radiator heating piping in white radiator varnish, two layers.
[5 empty] | m2 | 122 |  | 0
4. | Izolacija cevnog razvoda hladne vode prefabrikovanom izolacijom "Armaflex-AC" ili slično po metru dužine cevi. |  |  | 4. Insulation of cold water piping distribution network, with prefabricated 'Armaflex-AC' or equivalent, per m' of piping.
| f 26.9 x 2.3 |  | AF-4-028 (19 mm) | AF-4-028 (19 mm) | m' | 800 |  | 0
| f 33.7 x 2.6 |  | AF-4-035 (19,5 mm) | AF-4-035 (19,5 mm) | m' | 900 |  | 0
| f 42.4 x 2.9 |  | AF-4-042 (20,5 mm) | AF-4-042 (20,5 mm) | m' | 800 |  | 0
| f 48.3 x 2.9 |  | AF-4-048 (21 mm) | AF-4-048 (21 mm) | m' | 500 |  | 0
| f 60.3 x 2.9 |  | AF-4-060 (21,5 mm) | AF-4-060 (21,5 mm) | m' | 800 |  | 0
| f 76.1 x 2.9 |  | AF-4-076 (22 mm) | AF-4-076 (22 mm) | m' | 300 |  | 0
| f 88.9 x 3.2 |  | AF-4-089 (22,5 mm) | AF-4-089 (22,5 mm) | m' | 350 |  | 0
| f 114.1 x 3.6 |  | AF-4-114 (23,5 mm) | AF-4-114 (23,5 mm) | m' | 280 |  | 0
| f 139.7 x 4.0 |  | AF-4-140 (24,5 mm) | AF-4-140 (24,5 mm) | m' | 660 |  | 0
| f 168.3 x 4.5 |  | AF-4-168 (25 mm) | AF-4-168 (25 mm) | m' | 210 |  | 0
5. | Čišćenje čeličnom četkom i dvostruko mini- |  |  | 5. Cleaning with a steel brush and double red lead coating of cold water distribution piping.
ziranje celokupne cevne mreže razvoda hladne
vode.
[5 empty] | m2 | 950 |  | 0
6. | Izolacija cevnog razvoda po krovu objekta, od |  |  | 6. Insulation of piping distribution network along building roof, from chillers to air-contitioning unit, with 'Armaflex-AC' or equivalent type AF-4, coated in Al-sheet metal oe equivalent, per m' of piping.
rasladnih agregata do prostorije
klima centrale izolacijom "Armaflex-AC" ili slično
tip AF-4 u plaštu od Al-u lima ili slično po metru
dužine cevi.
| f 168.3 x 4.5 |  | AF-4-168 | AF-4-168 (25 mm) | m' | 90 |  | 0
7. | Probijanje otvora kroz zidove i međuspratnu |  |  | 7. Making of wall and floor slab hatches, with installation of distribution piping ribbed PVC framing, on breaches.
konstrukciju sa montažom štucni od rebra-
stih PVC cevi na razvodne cevi, na mestima
prodora
[5 empty] | kompl./set | 60 |  | 0
8. | Izrada i postavljene uramljene tehnološke šeme |  |  | 8. Production and exhibiting or framed technological diagram, on a prominent surface in the heating substation.
veze na vidno mesto u toplotnoj stanici
[5 empty] | paušalno/ lump sum | 1 |  | 0
9. | Regulacija ventila sa dvostrukom regulacijom |  |  | 9. Fine-tuning of double regulation valves to project specifications (for 39 g of Body)
na predviđene pozicije iz proračuna
(za 39 gr. Tela)
[5 empty] | paušalno/ lump sum | 1 |  | 0
10. | Predpodešavanje automatskih regulatora protoka i |  |  | 10. Fine-tuning of automatic flow controls and balance valves to project specified positions. (for 608 g of Body)
balans ventila na predviđene
pozicije iz proračuna
| (za 608 gr. Tela) |  |  |  | paušalno/ lump sum | 1 |  | 0
12. | Hladna proba instalacije (na čvrstoću) vodenim |  |  | 12. System pressure testing, Ppr=Prad+2 water pressure, 6 hours exposure, 24 hours monitoring. The contractor, supervising authority and investor are to produce a test log, upon testing.
pritiskom Ppr=Prad+2 bar u trajanju od šest časova
sa osmatranjem od 24 h. Po izvršenom ispitivanju
sačiniti zapisnik od strane izvođača radova, nadzornog organa i investitora.
[5 empty] | paušalno/ lump sum | 1 |  | 0
13. | Nabavka i punjenje instalacije mešavinom etilen |  |  | 13. Purchase and filling of installation with ethylene-glycol 30% and water mix.
glikola 30% i vode.
|  | mešavine |  |  | litara/lit | 3000 |  | 0
14. | Ispiranje cevne mreže hladnom vodom više puta, |  |  | 14. Flushing of piping system with cold water, multiple times, until clear water exits. The contractor, supervising authority and investor are to produce a work log.
sve dok ne pođe čista voda. Po izvršenom ispiranju
sačiniti zapisnik od strane izvođača radova, nadzornog organa i investitora.
[5 empty] | paušalno/ lump sum | 1 |  | 0
15. | Ispitivanje vazdušne propustljivosti prostora, u sve- |  |  | 15. Room air permeability testing, all in accordance with JUS U.J5.100. The contractor, carpentry subcontractor and central heating installation subcontractor are to produce a written report on works.
mu prema JUS-u U.J5.100. Po izvršenom ispitiva-
nju sačiniti Izveštaj od strane izvođača građ. radova,
kooperanta za ugradnju stolarije i izvođača instala-
cije centralnog grejanja.
[5 empty] | paušalno/ lump sum | 1 |  | 0
16. | Ispitivanje i merenje kvaliteta ugrađene termoizola- |  |  | 16. Testing and measuring of exteral wall thermal insulation quality, according to JUS U.J5.062. The contractor, installation subcontractor and central heating installation subcontractor are to produce a written report on works.
cije spoljnih zidova, prema JUS-u U.J5.062. Po
izvršenom ispitivanju sačiniti Izveštaj od strane
izvođača građ. radova, kooperanta za ugradnju
termoizolacije i izvođača instalacije centralnog
grejanja.
[5 empty] | paušalno/ lump sum | 1 |  | 0
17. | Pripremno završni radovi sa primopredajom |  |  | 17. Preparatory and finishing works, with installation handover; transport costs.
instalacije, transportni troškovi
[5 empty] | paušalno/ lump sum | 1 |  | 0
| Ukupno E: |  |  | Total E: |  |  |  | 0
| Rekapitulacija |  |  | Recapitulation
| A. RADIJATORSKO GREJANJE |  |  | A. RADIATOR HEATING
| A1. GREJNA TELA I PRIBOR |  |  | A1. HEATING UNITS AND ACCESSORIES |  |  |  | 0
| A2. CEVNA MREŽA I PRIBOR |  |  | A2. PIPEWORK AND ACCESSORIES |  |  |  | 0
| B. KLIMATIZACIJA |  |  | B. AIR-CONDITIONING
| B1. GREJNA/RASHLADNA TELA I PRIBOR |  |  | B1. HEATING/COOLING UNITS AND ACCESSORIES |  |  |  | 0
| B2. CEVNA MREŽA I PRIBOR |  |  | B2. PIPEWORK AND ACCESSORIES |  |  |  | 0
| C. PRIMARNA PODSTANICA |  |  | C. PRIMARY SUBSTATION |  |  |  | 0
| D. SEKUNDARNA PODSTANICA |  |  | D. SECONDARY SUBSTATION
| D1. SEKUNDARNA PODSTANICA 1 |  |  | D1. SECONDARY SUBSTATION 1 |  |  |  | 0
| D2. SEKUNDARNA PODSTANICA 5 |  |  | D2. SECONDARY SUBSTATION 5 |  |  |  | 0
| D3. SEKUNDARNA PODSTANICA 8 |  |  | D3. SECONDARY SUBSTATION 8 |  |  |  | 0
| D4. SEKUNDARNA PODSTANICA 9 |  |  | D4. SECONDARY SUBSTATION 9 |  |  |  | 0
| E. OSTALI RADOVI |  |  | E. OTHER WORKS |  |  |  | 0
| Ukupno FAZA I: |  |  | Total PHASE I: |  |  |  | 0